High Efficiency Flocculant POLYWEB P30

Appearance in Use	Standard POLYWEB P30 solution is clear colorless viscous liquid.

Appearance 		Solid POLYWEB P30 is for storage and transportation purpose, it is powder, high molecular weight

In Transportation 	polymers complex.

& Storage

Standard Solution		Use 2000 times of clean water (15~450C) to disperse solid POLYWEB P30 then to form the Standard POLYWEB P30

Solution. Add water first, and then slowly add solid POLYWEB P30 with agitation. Agitator speed should be

20~80rpm, agitating until uniform dispersion can be obtained (0.5~1 hour).

Application		Normal dosage may be 400~4000ml of Standard POLYWEB P30 Solution per m3 of wastewater, and

100~2000ml of Standard POLYWEB P30 Solution per m3of raw water for tap water. Exact dosage should

be determined by lab test or in system operations. The Standard POLYWEB P30 Solution should be pumped

to the addition points using a metering piston pump.

Property			Non-toxic, biodegradable and environmentally friendly.

Handling		The materials of handling should be plastic, stainless steel, fibreglass, etc.

Storage			Store in a cool, dry area. Keep container closed when not in use. Store temperature and

humidity are: 0~400C, RH<75%.

Safety			Do not take internally. Do not get in eyes, on skin, or on clothing. Wear chemically

resistant gloves. Slip when solid POLYWEB P30 or Standard POLYWEB P30 Solution spill on ground.

Validity			Storage: solid POLYWEB P30 can be stored longer than 1 year, may be 2~3 years based on the storage

conditions above. The Standard POLYWEB P30 Solution can be stored three days.

Function			Mainly used in E/F&P wastewater treatment technology. May be used in wastewater

treatment systems such as settlement, flotation, filtration, etc. The function of POLYWEB P30 is to

encapsulate, flocculate, adsorb and fixate the dirty particles in wastewater.

Treating Water		POLYWEB P30 can be used to treat various industrial wastewater, and also used in municipal wastewater

treatment systems,  tap water supply systems to improve efficiency.  POLYWEB P30 may combine with

other chemicals to obtain better results in some cases.

水处理高效絮聚剂 POLYWEB P30

使用状态	标准POLYWEB P30溶液是无色透明黏稠性液体。

储运状态	固态POLYWEB P30是为了储存和运输方便而使POLYWEB P30干化。固态POLYWEB P30是 颗粒粉末状态，混合型共聚物。

标准溶液	用2000倍干净水(水温15~450C)分散稀释固态POLYWEB P30便成标准POLYWEB P30溶液。先加好水于容器中，

然后边搅拌边一点点加入POLYWEB P30，搅拌转速20~80rpm，不宜强力搅拌。搅拌直至完全均匀

分散(0.5~1小时)。

使	用	一般每吨废水用 400~4000毫升标准POLYWEB P30溶液，每吨自来水源水用 100~2000毫升标准POLYWEB P30

溶液。(根据水质情况实验室或实际操作确定其确切用量)。用低剪切力泵(正向位移泵)

或利用高位差把标准POLYWEB P30溶液输送至加入点。标准POLYWEB P30溶液的加入点一般在所有其它药剂

加完之后，应有足够时间与污水充分混合。

性	质	无毒无害，生物可降解，符合饮用水卫生标准。

包	装	用塑料作为其盛装材料即可，用不锈钢、纤维玻璃或玻璃均可。

储	存	应放于阴凉干燥处，密封，不可晒，须防潮。温度0至40度C，湿度75%以下。

安	全	不要入口眼鼻。标准POLYWEB P30溶液和固态POLYWEB P30撒于地下会滑。操作时须带手套。不慎入眼，

要清水冲洗15分钟以上。皮肤接触，清水或肥皂水冲洗。如果误食，需喝大量水或牛

奶，并看医生。

保  存   期	按上述储存条件，固态POLYWEB P30可保存最少一年，可达两至三年；标准POLYWEB P30溶液可存放三天。

功	能	主要用于配合 E/F & P污水处理技术使用。亦可直接用于沉降、气浮或过滤污水处理系

统。作用是囊包、絮聚、定着和吸附污水中的污物。

适用污水	POLYWEB P30可用于工业污水处理，市政污水处理，也可用于自来水净化，糖汁净化，等等，提

高系统效率。具体有些场合需与其它化学剂合用，以达到最佳效果。